5-7 Sidewall Standard Spray Sprinklers.

5-7.2 Protection Areas per Sprinkler (Standard Sidewall Spray Sprinklers).

5-7.2.1 Definition of the protection Aria of Coverage.

5-7.2.1.1  The protection area of coverage per sprinkler (As) shall be determined as follows:

- Along the Wall. Determine the distance between sprinklers along the wall (or to the end or obstruction in the case of the end sprinkler on the branch line) upstream and downstream. Choose the larger of either twice the distance to the end wall or the distance to the next sprinkler. This dimension will be defined as S.

- Across the Room. Determine the distance from the sprinkler to the wall opposite the sprinklers or to the midpoint of the room where sprinklers are installed on two opposite walls (see 5-7.3.1) This dimension will be defined as L.

5-7.2.1.2 The protection area of the sprinkler shall be established by multiplying the S dimension by the L dimension, as follows: As = S x L

5-7.2.2  Maximum Protection Area of Coverage. The maximum allowable protection area of coverage for a sprinkler (As) shell be accordance with the value indicated in the table 5-7.2.2. In any case, the maximum area of coverage of a sprinkler shall not exceed 196 ft2 (59.7 m2).

|  | Light Hazard |  | Ordinary Hazard |  |
| --- | --- | --- | --- | --- |
|  | Combustible Finish | Noncombustible or Limited-Combustible Finish | Combustible Finish | Noncombustible or Limited-Combustible Finish |
| Maximum distance along the wall (S) | 14ft | 14ft | 10ft | 10ft |
| Maximum room width (L) | 12ft | 14ft | 10ft | 10ft |
| Maximum protection area | 120 ft2 | 196 ft2 | 80 ft2 | 100 ft2 |

Table 5-7.2.2

5-7.3   Sprinkler Spacing (Standard Sidewall Spray Sprinklers)

5-7.3.1 Maximum distance between sprinklers.

5-7.3.1.1 The maximum distance permitted between sprinklers shall be based on the centerline distance between sprinklers on the branch line. The maximum distance shall be measured along the slope of the ceiling.

5-7.3.1.2 Sidewall spray sprinklers shall be installed along the length of a single wall of rooms or bays in accordance with the maximum spacing provisions of Table 5-7.2.2.

Exception #1: Sidewall sprinklers shall not be installed back-to-back without being separated by a continuous lintel or soffit.

Exception #2: Where the width of the room or bay exceeds the maximum allowed, up to 24ft (7.32m) for light hazard occupancy or 20ft (6.1m) for ordinary hazard occupancy sidewall sprinklers shall be provided on two opposite walls or sides of bays with spacing as required by Table 5-7.2.2.

Exception #3: Sidewall sprinklers shall be permitted to be installed on opposing or adjacent wall provided no sprinkler is located within the maximum protection area of another sprinkler.

5-7.3.2 Maximum Distance from Wall. The distance from sprinklers to the and walls shall not exceed one-half of the allowable distance permitted between sprinklers as in Table 5-7.2.2.

5-7.3.3 Minimum Distance from Wall. Min 4in (102mm) from an end wall.

5-7.3.4 Minimum Distance Between Sprinklers. Not less than 6ft (1.8m) on center.

5-7.4   Deflector Position from Ceiling and Wall (Standard Sidewall Spray Sprinklers).

5-7.4.1 Distance Below Ceiling and from Walls.

5-7.4.1.1  Sidewall sprinkler deflectors shell be located not more than 6in. (152mm) or less than 4in. (102mm) for ceilings.

Exception: Horizontal sidewall sprinklers shall be permitted to be located in a zone 6in. to 12in. (152mm to 305mm) below noncombustible and limited-combustible ceiling listed for such use.

5-7.4.1.3    Sidewall sprinklers shall only be installed along wall, lintels, or soffits where the distance from the ceiling to the bottom of the lintel or soffit is at least 2in (51mm) greater than the distance from the ceiling to sidewall sprinkler deflectors.

Ceiling

Y

X

X ≥ 2in. (51mm) + Y

Y (see 5-7.4.1.1)

Z ≤ 8in (203mm) (see 5-7.4.1.4)

Z

Elevation View

Exhibit  5.21 Installation of sidewall sprinkler along the soffit.

Wall

5-7.4.1.4 Where soffits are used for the installation of sidewall sprinklers, they shall not exceed 8in (203mm) in width or projection from the wall.

Exception: Soffit shall be permitted to exceed 8in (203mm) where additional sprinklers are installed bellow the soffit.

5-7.4.2 Deflector Orientation.

5-7.4.2.1 Deflectors of sprinklers shall be aligned parallel to ceilings or roofs.

5-7.4.2.2 Sidewall sprinklers, where installed under a sloped ceiling, shall be located at the high point of the slope and positioned to discharge downward along the slope.

5-7.5 Obstructions to Sprinkler Discharge (Standard Sidewall Spray Sprinklers).

5-7.5.1 Performance Objective.

5-7.5.1.1   Sprinklers shall be located so as to minimize obstructions to discharge as defined in 5-5.5.2 and 5-5.5.3, or additional sprinklers shall be provided to ensure adequate coverage of hazard.

5-7.5.1.2  Sidewall sprinklers shall be installed no closer than 4ft (1.2m) from light fixtures or similar obstructions. The distance between light fixtures or similar obstructions located more than 4ft (1.2m) from the sprinkler shall be in conformity with Table 5-7.5.1.2 and Figure 5-7.5.1.2.

Table 5-7.5.1.2 Positioning of Sprinklers to Avoid Obstructions (Standard Sidewall Spray Sprinklers)

| Distance from Sidewall Sprinkler to Side of Objection (A) | Maximum Allowable Distance of Deflector above Bottom of Objection (in.)(B) |
| --- | --- |
| Less than 4ft 4ft to less than 5ft 5ft to less than 5ft 6in 5ft 6in to less than 6ft 6ft to less than 6ft 6in 6ft 6in to less than 7ft 7ft to less than 7ft 6in 7ft 6in to less than 8ft 8ft to less than 8ft 6in 8ft 6in or greater | 0 1 2 3 4 6 7 9 11 14 |

Obstruction

Ceiling or Roofing

B

Elevation View

A

Wall

Figure 5-7.5.1.2 Positioning of sprinklers to avoid obstructions (standard sidewall spray sprinklers).

5-7.5.1.3   Obstruction projecting from the same wall as the one on which the sidewall sprinkler is mounted shall be in accordance with Table 5-7.5.1.3 and Figure 5-7.5.1.3.

Table 5-7.5.1.3 Positioning of Sprinklers to Avoid Obstructions Along the Wall (Standard Sidewall Spray Sprinklers).

| Distance from Sidewall Sprinkler to Side of Obstruction (A) | Maximum Allowable Distance of Deflector above Bottom of Obstruction (in.)(B) |
| --- | --- |
| Less than 6in. 6in to less than 1ft 1ft to less than 1ft 6in 1ft 6in to less than 2ft 2ft in to less than 2ft 6in 2ft 6in to less than 3ft 3ft to less than 3ft 6in 3ft 6in to less than 4ft 4ft to less than 4ft 6in 4ft 6in to less than 5ft 5ft to less than 5ft 6in 5ft 6in to less than 6ft 6ft to less than 6ft 6in 6ft 6in to less than 7ft 7ft to less than 7ft 6in | 1 2 3 4 ½ 5 ¾ 7 8 9 ¼ 10 11 ½ 12 ¾ 14 15 16 ¼ 17 ½ |

Obstruction

Ceiling

Sidewall sprinkler on wall

B

A

Elevation View

Figure 5-7.5.1.3 Positioning of sprinklers to avoid obstructions along the wall (standard sidewall spray sprinklers).

5-7.5.2 Obstructions to Sprinkler Discharge Pattern Development.

5-7.5.2.1* Continuous or noncontinuous obstructions less than or equal to 18in. (457mm) below the sprinkler deflector that that prevent the pattern from fully developing shall comply with this section. Regardless of the rules of this section, solid continuous obstructions shall meet the requirements of 5-7.5.1.2.

A-5-7.5.2.1   The rules of 5-7.5.2.2 (known as the “Three Times Rule”) have been written to apply to obstructions where the sprinkler can be expected to get water to both sides of the obstruction without allowing a significant dry shadow on the other side of the obstruction. This works for small noncontinuous obstructions and for continuous obstructions where the sprinkler can throw water over and under the obstruction, such as the bottom chord of an open truss or joist. For solid continuous obstructions, such as abeam, the “Three Times Rule” is ineffective since the sprinkler cannot throw water over and under the obstruction. Sufficient water must be thrown under the obstruction to adequately cover the floor area on the other side of the obstruction. To ensure this, compliance with the rules of 5-7.5.1.2 is necessary.

5-7.5.2.2   Sprinklers shall be positioned such that they are located at a distance three times greater than the maximum dimension of an obstruction up to a maximum of 24in. (609mm) (e.g., truss webs and chords, pipe, columns, and fixtures). Sidewall sprinklers shall be positioned in accordance with Figure 5-7.5.2.2 where obstructions are present.

Exception #1: Piping to which sidewall sprinklers are directly attached.

Exception #2: Sprinklers positioned with respect to obstructions in accordance with 5-7.5.1.2 and 5-7.5.1.3.

D

Sprinkler

Ceiling

Obstruction

A

C

C

D

A

Wall

Wall

Plan View of Column                                                   Elevation View of Pipe Conduit or Light Fixture

A ≥ 3C or 3D       A ≤ 24in

(Use dimension C or D, whichever is greater)

5-7.5.2.3   Suspended or Floor-Mounted Vertical Obstructions. The distance from sprinklers to privacy curtains, free-standing partition, room dividers, and similar obstructions in light hazard occupancies shall be in accordance with Table 5-7.5.2.3 and Figure 5-7.5.2.3.

Table 5-7.5.2.3   Suspended or Floor-Mounted Obstructions (Standard Spray Sprinklers)

| Horizontal Distance (A) | Minimum Vertical Distance below Deflector (in)(B) |
| --- | --- |
| 6in. or less More than 6in. to 9in More than 6in. to 12in More than 12in. to 15in More than 15in. to 18in More than 18in. to 24in More than 24in. to 30in More than 30in. | 3 4 6 8 9 ½ 12 ½ 15 ½ 18 |

Ceiling

B

A

Obstruction

Wall

Floor

Figure 5-7.5.2.3 Suspended or Floor-Mounted Obstructions (Standard Sidewall Spray Sprinklers).

5-7.5.3* Obstructions that Prevent Sprinkler Discharge from Reaching the Hazard.

A-5-7.5.3    See A-5-5.5.3.

5-7.5.3.1   Continuous or noncontinuous obstructions that interrupt the water discharge in a horizontal plane more than 18in. (457mm) below the sprinkler deflector in a manner to limit the distribution from reaching the protected hazard shall comply with this section.

5-7.5.3.2   Sprinklers shall be installed under fixed obstructions over 4ft (1.2m) wide such as duct, desk, open grate flooring cutting tables, and overhead door.

Exception: Obstructions that are not fixed in place such as conference tables.

5-7.6   Clearance to storage (Standard Sidewall Spray Sprinklers).

The clearance between the deflector and the top of storage shall be 18in (457mm) or greater.